How the two devices work. The AG-1250E is a powered sensor with an internal SPDT relay. RED and BLACK are its 24 VAC supply. The relay's common is the RED hot, PURPLE is the normally closed contact (5 A) and WHITE is the normally open contact (1 A). When it senses water, WHITE becomes 24 VAC hot. The IoT Relay's control input accepts 3 to 48 VDC or 12 to 120 VAC on its two terminals, optically isolated, with no jumpers; on AC the + and − marking does not matter. It draws about 1.1 W when activated, roughly 45 mA at 24 VAC, well inside the WHITE contact's 1 A.

Connections at the control panel end of the five-wire cable

┌────────────┬─────────────────────────────┬───────────────────────────────┐

│ Cable wire │           Far end           │           Panel end           │

├────────────┼─────────────────────────────┼───────────────────────────────┤

│ Red        │ AG RED, 24 VAC hot in       │ Transformer hot               │

├────────────┼─────────────────────────────┼───────────────────────────────┤

│ Blue       │ AG BLACK, 24 VAC common in  │ Transformer common            │

├────────────┼─────────────────────────────┼───────────────────────────────┤

│ White      │ AG WHITE, normally open out │ Splice to cable green         │

├────────────┼─────────────────────────────┼───────────────────────────────┤

│ Green      │ IoT +                       │ Splice to cable white         │

├────────────┼─────────────────────────────┼───────────────────────────────┤

│ Yellow     │ IoT −                       │ Transformer common, with blue │

└────────────┴─────────────────────────────┴───────────────────────────────┘

Cap the AG's PURPLE wire; it is unused. Dry, the IoT input sees 0 V between green and yellow. Wet, WHITE carries the hot through the closed contact, so the input sees 24 VAC and the relay trips. Plug the Scala into one of the IoT Relay's normally on outlets so water detection removes its power; the normally off pair could run an alarm.

Confirm it with a meter before trusting it: with the sensor powered and dry, white to blue reads 0 V; bridge the sensor's metal contacts with a wet finger and it reads 24 VAC, and the IoT Relay's input LED lights. The sensor draws continuously, so the transformer must stay on.